## YJLV32 英
0.6/1kV-1 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 0.7 | 0.8 | 1.8 | 13.2 | 287 | 3.08 | 38.5 | 52.5
1X16 | 0.7 | 0.8 | 1.8 | 14.3 | 336 | 1.91 | 49.7 | 67.9
1X25 | 0.9 | 0.8 | 1.8 | 16 | 417 | 1.2 | 65.8 | 87.5
1X35 | 0.9 | 1.25 | 1.8 | 17.5 | 575 | 0.868 | 80.5 | 105
1X50 | 1 | 1.25 | 1.8 | 19 | 673 | 0.641 | 98 | 122.5
1X70 | 1.1 | 1.25 | 1.8 | 20.8 | 800 | 0.443 | 126 | 150.5
1X95 | 1.1 | 1.6 | 1.8 | 23.1 | 1065 | 0.32 | 154 | 182
1X120 | 1.2 | 1.6 | 1.8 | 24.7 | 1212 | 0.253 | 182 | 206.5
1X150 | 1.4 | 1.6 | 1.8 | 26.6 | 1398 | 0.206 | 210 | 234.5
1X185 | 1.6 | 1.6 | 1.8 | 28.8 | 1610 | 0.164 | 245 | 266
1X240 | 1.7 | 1.6 | 1.9 | 31.3 | 1890 | 0.125 | 289.8 | 311.5
1x300 | 1.8 | 2 | 2 | 34.7 | 2434 | 0.1 | 339.5 | 353.5
1x400 | 2 | 2 | 2.2 | 38.7 | 2946 | 0.0778 | 399 | 402.5
1x500 | 2.2 | 2 | 2.3 | 42.9 | 3549 | 0.0605 | 469 | 465.5
1X630 | 2.4 | 2.5 | 2.4 | 48 | 4595 | 0.0469 | 553 | 532
1X800 | 2.6 | 2.5 | 2.6 | 52.7 | 5459 | 0.0367 | 644 | 612.5
0.6/1kV-2 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.7 | 0.8 | 1.8 | 14.8 | 333 | 12.1 | 17.5 | 25.2
2X4 | 0.7 | 0.8 | 1.8 | 15.7 | 375 | 7.41 | 23.8 | 32.9
2X6 | 0.7 | 1.25 | 1.8 | 17.6 | 570 | 4.61 | 31.5 | 42.7
2X10 | 0.7 | 1.25 | 1.8 | 20.1 | 677 | 3.08 | 40.6 | 54.6
2X16 | 0.7 | 1.25 | 1.8 | 22.3 | 808 | 1.91 | 52.5 | 70
2X25 | 0.9 | 1.6 | 1.8 | 26.3 | 1170 | 1.2 | 70 | 91
2X35 | 0.9 | 1.6 | 1.8 | 27.6 | 1287 | 0.868 | 84 | 108.5
2X50 | 1 | 1.6 | 1.9 | 30.8 | 1548 | 0.641 | 105 | 129.5
2X70 | 1.1 | 2 | 2 | 35.4 | 2150 | 0.443 | 133 | 157.5
2X95 | 1.1 | 2 | 2.1 | 39.5 | 2600 | 0.32 | 164.5 | 192.5
2X120 | 1.2 | 2 | 2.3 | 42.9 | 3003 | 0.253 | 192.5 | 220.5
2X150 | 1.4 | 2.5 | 2.4 | 48 | 3919 | 0.206 | 220.5 | 245
2X185 | 1.6 | 2.5 | 2.6 | 52.7 | 4562 | 0.164 | 255.5 | 276.5
0.6/1kV-3 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.7 | 0.8 | 1.8 | 15.3 | 358 | 12.1 | 15.4 | 21.7
3X4 | 0.7 | 0.8 | 1.8 | 16.2 | 406 | 7.41 | 20.3 | 28
3X6 | 0.7 | 1.25 | 1.8 | 18.3 | 584 | 4.61 | 27.3 | 36.4
3X10 | 0.7 | 1.25 | 1.8 | 20.9 | 741 | 3.08 | 35 | 46.2
3X16 | 0.7 | 1.25 | 1.8 | 23.3 | 891 | 1.91 | 45.5 | 59.5
3X25 | 0.9 | 1.6 | 1.8 | 27.6 | 1295 | 1.2 | 60.9 | 77
3X35 | 0.9 | 1.6 | 1.8 | 29 | 1465 | 0.868 | 73.5 | 91
3X50 | 1 | 1.6 | 1.9 | 32.5 | 1765 | 0.641 | 91 | 112
3X70 | 1.1 | 2 | 2.1 | 37.9 | 2488 | 0.443 | 115.5 | 136.5
3X95 | 1.1 | 2 | 2.2 | 41.8 | 2982 | 0.32 | 143.5 | 164.5
3X120 | 1.2 | 2 | 2.3 | 45.5 | 3465 | 0.253 | 168 | 185.5
3X150 | 1.4 | 2.5 | 2.5 | 51.3 | 4606 | 0.206 | 189 | 210
3X185 | 1.6 | 2.5 | 2.7 | 55.9 | 5317 | 0.164 | 220.5 | 238
3X240 | 1.7 | 2.5 | 2.9 | 62.1 | 6403 | 0.125 | 262.5 | 276.5
3X300 | 1.8 | 2.5 | 3 | 67.4 | 7430 | 0.1 | 304.5 | 311.5
0.6/1kV-4 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.7 | 0.8 | 1.8 | 16.1 | 409 | 12.1 | 15.4 | 21.7
4X4 | 0.7 | 1.25 | 1.8 | 18.1 | 577 | 7.41 | 20.3 | 28
4X6 | 0.7 | 1.25 | 1.8 | 19.3 | 655 | 4.61 | 27.3 | 36.4
4X10 | 0.7 | 1.25 | 1.8 | 22.3 | 838 | 3.08 | 35 | 46.2
4X16 | 0.7 | 1.6 | 1.8 | 25.7 | 1171 | 1.91 | 45.5 | 59.5
4X25 | 0.9 | 1.6 | 1.8 | 29.7 | 1482 | 1.2 | 60.9 | 77
4X35 | 0.9 | 1.6 | 1.9 | 31.4 | 1692 | 0.868 | 73.5 | 91
4X50 | 1 | 1.6 | 2 | 35.3 | 2062 | 0.641 | 91 | 112
4X70 | 1.1 | 2 | 2.2 | 41.2 | 2918 | 0.443 | 115.5 | 136.5
4X95 | 1.1 | 2 | 2.3 | 45.6 | 3505 | 0.32 | 143.5 | 164.5
4X120 | 1.2 | 2.5 | 2.5 | 51.2 | 4652 | 0.253 | 168 | 185.5
4X150 | 1.4 | 2.5 | 2.7 | 56.1 | 5425 | 0.206 | 189 | 210
4X185 | 1.6 | 2.5 | 2.8 | 61.3 | 6313 | 0.164 | 220.5 | 238
4X240 | 1.7 | 2.5 | 3.1 | 68.1 | 7655 | 0.125 | 262.5 | 276.5
4X300 | 1.8 | 2.5 | 3.2 | 74.1 | 8945 | 0.1 | 304.5 | 311.5
0.6/1kV-5 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.7 | 1.25 | 1.8 | 17.9 | 567 | 12.1 | 15.4 | 21.7
5X4 | 0.7 | 1.25 | 1.8 | 19.1 | 645 | 7.41 | 20.3 | 28
5X6 | 0.7 | 1.25 | 1.8 | 20.5 | 736 | 4.61 | 27.3 | 36.4
5X10 | 0.7 | 1.6 | 1.8 | 24.6 | 1098 | 3.08 | 35 | 46.2
5X16 | 0.7 | 1.6 | 1.8 | 27.6 | 1311 | 1.91 | 45.5 | 59.5
5X25 | 0.9 | 1.6 | 1.9 | 32.2 | 1708 | 1.2 | 60.9 | 77
5X35 | 0.9 | 1.6 | 2 | 34.1 | 1955 | 0.868 | 73.5 | 91
5X50 | 1 | 2 | 2.2 | 39.7 | 2726 | 0.641 | 91 | 112
5X70 | 1.1 | 2 | 2.3 | 44.9 | 3376 | 0.443 | 115.5 | 136.5
5X95 | 1.1 | 2.5 | 2.5 | 51.3 | 4633 | 0.32 | 143.5 | 164.5
5X120 | 1.2 | 2.5 | 2.7 | 55.9 | 5394 | 0.253 | 168 | 185.5
5X150 | 1.4 | 2.5 | 2.8 | 61.4 | 6340 | 0.206 | 189 | 210
5X185 | 1.6 | 2.5 | 3 | 67.6 | 7488 | 0.164 | 220.5 | 238
5X240 | 1.7 | 2.5 | 3.3 | 74.8 | 9038 | 0.125 | 262.5 | 276.5
5X300 | 1.8 | 3.15 | 3.5 | 83.2 | 11646 | 0.1 | 304.5 | 311.5
0.6/1kV-3+1 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+1X2.5 | 0.7/0.7 | 1.25 | 1.8 | 17.8 | 589 | 7.41/12.1 | 20.3 | 28
3X6+1X4 | 0.7/0.7 | 1.25 | 1.8 | 19.1 | 627 | 4.61/7.41 | 27.3 | 36.4
3X10+1X6 | 0.7/0.7 | 1.25 | 1.8 | 21.6 | 777 | 3.08/4.61 | 35 | 46.2
3X16+1X10 | 0.7/0.7 | 1.6 | 1.8 | 25.1 | 1111 | 1.91/3.08 | 45.5 | 59.5
3X25+1X16 | 0.9/0.7 | 1.6 | 1.8 | 28.7 | 1541 | 1.2/1.91 | 60.9 | 77
3X35+1X16 | 0.9/0.7 | 1.6 | 1.8 | 30 | 1561 | 0.868/1.91 | 73.5 | 91
3X50+1X25 | 1/0.9 | 1.6 | 2 | 34.1 | 1925 | 0.641/1.2 | 91 | 112
3X70+1X35 | 1.1/0.9 | 2 | 2.1 | 39.2 | 2669 | 0.443/0.868 | 115.5 | 136.5
3X95+1X50 | 1.1/1.0 | 2 | 2.3 | 43.2 | 3203 | 0.32/0.641 | 143.5 | 164.5
3X120+1X70 | 1.2/1.1 | 2.5 | 2.4 | 48.8 | 4225 | 0.253/0.443 | 168 | 185.5
3X150+1X70 | 1.4/1.1 | 2.5 | 2.6 | 52.9 | 4815 | 0.206/0.443 | 189 | 210
3X185+1X95 | 1.6/1.1 | 2.5 | 2.7 | 57.8 | 5696 | 0.164/0.32 | 220.5 | 238
3X240+1X120 | 1.7/1.2 | 2.5 | 2.9 | 64.1 | 6827 | 0.125/0.253 | 262.5 | 276.5
3X300+1X150 | 1.8/1.4 | 2.5 | 3.1 | 69.8 | 8005 | 0.1/0.206 | 304.5 | 311.5
0.6/1kV-4+1 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X4+1X2.5 | 0.7/0.7 | 1.25 | 1.8 | 18.9 | 615 | 7.41/12.1 | 20.3 | 28
4X6+1X4 | 0.7/0.7 | 1.25 | 1.8 | 20.3 | 699 | 4.61/7.41 | 27.3 | 36.4
4X10+1X6 | 0.7/0.7 | 1.6 | 1.8 | 23.9 | 1007 | 3.08/4.61 | 35 | 46.2
4X16+1X10 | 0.7/0.7 | 1.6 | 1.8 | 27 | 1250 | 1.91/3.08 | 45.5 | 59.5
4X25+1X16 | 0.9/0.7 | 1.6 | 1.9 | 31.2 | 1609 | 1.2/1.91 | 60.9 | 77
4X35+1X16 | 0.9/0.7 | 1.6 | 1.9 | 32.8 | 1808 | 0.868/1.91 | 73.5 | 91
4X50+1X25 | 1/0.9 | 2 | 2.1 | 38.5 | 2555 | 0.641/1.2 | 91 | 112
4X70+1X35 | 1.1/0.9 | 2 | 2.3 | 43 | 3135 | 0.443/0.868 | 115.5 | 136.5
4X95+1X50 | 1.1/1.0 | 2.5 | 2.4 | 48.9 | 4247 | 0.32/0.641 | 143.5 | 164.5
4X120+1X70 | 1.2/1.1 | 2.5 | 2.6 | 54 | 5065 | 0.253/0.443 | 168 | 185.5
4X150+1X70 | 1.4/1.1 | 2.5 | 2.7 | 58.4 | 5750 | 0.206/0.443 | 189 | 210
4X185+1X95 | 1.6/1.1 | 2.5 | 2.9 | 64.4 | 6865 | 0.164/0.32 | 220.5 | 238
4X240+1X120 | 1.7/1.2 | 2.5 | 3.1 | 71.1 | 8196 | 0.125/0.253 | 262.5 | 276.5
4X300+1X150 | 1.8/1.4 | 3.15 | 3.4 | 78.9 | 10523 | 0.1/0.206 | 304.5 | 311.5
0.6/1kV-3+2 core aluminum conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+2X2.5 | 0.7/0.7 | 1.25 | 1.8 | 18.6 | 597 | 7.41/12.1 | 20.3 | 28
3X6+2X4 | 0.7/0.7 | 1.25 | 1.8 | 20 | 680 | 4.61/7.41 | 27.3 | 36.4
3X10+2X6 | 0.7/0.7 | 1.25 | 1.8 | 22.5 | 846 | 3.08/4.61 | 35 | 46.2
3X16+2X10 | 0.7/0.7 | 1.6 | 1.8 | 26.5 | 1205 | 1.91/3.08 | 45.5 | 59.5
3X25+2X16 | 0.9/0.7 | 1.6 | 1.8 | 30.2 | 1523 | 1.2/1.91 | 60.9 | 77
3X35+2X16 | 0.9/0.7 | 1.6 | 1.9 | 31.3 | 1666 | 0.868/1.91 | 73.5 | 91
3X50+2X25 | 1/0.9 | 2 | 2.1 | 37 | 2415 | 0.641/1.2 | 91 | 112
3X70+2X35 | 1.1/0.9 | 2 | 2.2 | 41.1 | 2897 | 0.443/0.868 | 115.5 | 136.5
3X95+2X50 | 1.1/1.0 | 2 | 2.4 | 45.8 | 3527 | 0.32/0.641 | 143.5 | 164.5
3X120+2X70 | 1.2/1.1 | 2.5 | 2.6 | 52.1 | 4745 | 0.253/0.443 | 168 | 185.5
3X150+2X70 | 1.4/1.1 | 2.5 | 2.7 | 55.4 | 5238 | 0.206/0.443 | 189 | 210
3X185+2X95 | 1.6/1.1 | 2.5 | 2.8 | 60.8 | 6238 | 0.164/0.32 | 220.5 | 238
3X240+2X120 | 1.7/1.2 | 2.5 | 3 | 67.4 | 7495 | 0.125/0.253 | 262.5 | 276.5
3X300+2X150 | 1.8/1.4 | 2.5 | 3.2 | 73.6 | 8767 | 0.1/0.206 | 304.5 | 311.5

## YJV32 英
0.6/1kV-1 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 0.7 | 0.8 | 1.8 | 13.2 | 350 | 1.83 | 50 | 68.6
1X16 | 0.7 | 0.8 | 1.8 | 14.3 | 436 | 1.15 | 65 | 87.5
1X25 | 0.9 | 0.8 | 1.8 | 16 | 566 | 0.727 | 84 | 112
1X35 | 0.9 | 1.25 | 1.8 | 17.5 | 785 | 0.524 | 105 | 133
1X50 | 1 | 1.25 | 1.8 | 19 | 960 | 0.387 | 126 | 161
1X70 | 1.1 | 1.25 | 1.8 | 20.8 | 1211 | 0.268 | 161 | 196
1X95 | 1.1 | 1.6 | 1.8 | 23.1 | 1632 | 0.193 | 199.5 | 234.5
1X120 | 1.2 | 1.6 | 1.8 | 24.7 | 1935 | 0.153 | 234.5 | 269.5
1X150 | 1.4 | 1.6 | 1.8 | 26.6 | 2307 | 0.124 | 269.5 | 301
1X185 | 1.6 | 1.6 | 1.8 | 28.8 | 2730 | 0.0991 | 315 | 343
1X240 | 1.7 | 1.6 | 1.9 | 31.3 | 3358 | 0.0754 | 374.5 | 399
1x300 | 1.8 | 2 | 2 | 34.7 | 4277 | 0.0601 | 434 | 451.5
1x400 | 2 | 2 | 2.2 | 38.7 | 5362 | 0.047 | 504 | 514.5
1x500 | 2.2 | 2 | 2.3 | 42.9 | 6650 | 0.0366 | 584.5 | 588
1X630 | 2.4 | 2.5 | 2.4 | 48 | 8512 | 0.0283 | 672 | 665
1X800 | 2.6 | 2.5 | 2.6 | 52.7 | 10440 | 0.0221 | 777 | 756
0.6/1kV-2 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.7 | 0.8 | 1.8 | 14.8 | 364 | 7.41 | 23.1 | 32.2
2X4 | 0.7 | 0.8 | 1.8 | 15.7 | 425 | 4.61 | 30.1 | 41.3
2X6 | 0.7 | 1.25 | 1.8 | 17.6 | 646 | 3.08 | 38.5 | 52.5
2X10 | 0.7 | 1.25 | 1.8 | 20.1 | 802 | 1.83 | 53.2 | 70
2X16 | 0.7 | 1.25 | 1.8 | 22.3 | 1008 | 1.15 | 67.9 | 91
2X25 | 0.9 | 1.6 | 1.8 | 26.3 | 1470 | 0.727 | 91 | 115.5
2X35 | 0.9 | 1.6 | 1.8 | 27.6 | 1712 | 0.524 | 112 | 140
2X50 | 1 | 1.6 | 1.9 | 30.8 | 2123 | 0.387 | 136.5 | 168
2X70 | 1.1 | 2 | 2 | 35.4 | 2974 | 0.268 | 171.5 | 203
2X95 | 1.1 | 2 | 2.1 | 39.5 | 3737 | 0.193 | 214.2 | 248.5
2X120 | 1.2 | 2 | 2.3 | 42.9 | 4453 | 0.153 | 248.5 | 283.5
2X150 | 1.4 | 2.5 | 2.4 | 48 | 5744 | 0.124 | 283.5 | 315
2X185 | 1.6 | 2.5 | 2.6 | 52.7 | 6811 | 0.0991 | 325.5 | 357
0.6/1kV-3 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.7 | 0.8 | 1.8 | 15.3 | 405 | 7.41 | 19.6 | 27.3
3X4 | 0.7 | 0.8 | 1.8 | 16.2 | 481 | 4.61 | 25.9 | 35.7
3X6 | 0.7 | 1.25 | 1.8 | 18.3 | 696 | 3.08 | 32.9 | 44.8
3X10 | 0.7 | 1.25 | 1.8 | 20.9 | 930 | 1.83 | 45.5 | 60.2
3X16 | 0.7 | 1.25 | 1.8 | 23.3 | 1191 | 1.15 | 58.8 | 77
3X25 | 0.9 | 1.6 | 1.8 | 27.6 | 1745 | 0.727 | 77 | 98
3X35 | 0.9 | 1.6 | 1.8 | 29 | 2100 | 0.524 | 94.5 | 119
3X50 | 1 | 1.6 | 1.9 | 32.5 | 2628 | 0.387 | 119 | 143.5
3X70 | 1.1 | 2 | 2.1 | 37.9 | 3728 | 0.268 | 150.5 | 175
3X95 | 1.1 | 2 | 2.2 | 41.8 | 4692 | 0.193 | 185.5 | 210
3X120 | 1.2 | 2 | 2.3 | 45.5 | 5645 | 0.153 | 217 | 241.5
3X150 | 1.4 | 2.5 | 2.5 | 51.3 | 7350 | 0.124 | 245 | 269.5
3X185 | 1.6 | 2.5 | 2.7 | 55.9 | 8698 | 0.0991 | 283.5 | 304.5
3X240 | 1.7 | 2.5 | 2.9 | 62.1 | 10837 | 0.0754 | 336 | 350
3X300 | 1.8 | 2.5 | 3 | 67.4 | 12990 | 0.0601 | 388.5 | 395.5
0.6/1kV-4 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.7 | 0.8 | 1.8 | 16.1 | 472 | 7.41 | 19.6 | 27.3
4X4 | 0.7 | 1.25 | 1.8 | 18.1 | 677 | 4.61 | 25.9 | 35.7
4X6 | 0.7 | 1.25 | 1.8 | 19.3 | 804 | 3.08 | 32.9 | 44.8
4X10 | 0.7 | 1.25 | 1.8 | 22.3 | 1088 | 1.83 | 45.5 | 60.2
4X16 | 0.7 | 1.6 | 1.8 | 25.7 | 1571 | 1.15 | 58.8 | 77
4X25 | 0.9 | 1.6 | 1.8 | 29.7 | 2085 | 0.727 | 77 | 98
4X35 | 0.9 | 1.6 | 1.9 | 31.4 | 2543 | 0.524 | 94.5 | 119
4X50 | 1 | 1.6 | 2 | 35.3 | 3214 | 0.387 | 119 | 143.5
4X70 | 1.1 | 2 | 2.2 | 41.2 | 4571 | 0.268 | 150.5 | 175
4X95 | 1.1 | 2 | 2.3 | 45.6 | 5782 | 0.193 | 185.5 | 210
4X120 | 1.2 | 2.5 | 2.5 | 51.2 | 7557 | 0.153 | 217 | 241.5
4X150 | 1.4 | 2.5 | 2.7 | 56.1 | 9080 | 0.124 | 245 | 269.5
4X185 | 1.6 | 2.5 | 2.8 | 61.3 | 10822 | 0.0991 | 283.5 | 304.5
4X240 | 1.7 | 2.5 | 3.1 | 68.1 | 13566 | 0.0754 | 336 | 350
4X300 | 1.8 | 2.5 | 3.2 | 74.1 | 16356 | 0.0601 | 388.5 | 395.5
0.6/1kV-5 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.7 | 1.25 | 1.8 | 17.9 | 645 | 7.41 | 19.6 | 27.3
5X4 | 0.7 | 1.25 | 1.8 | 19.1 | 770 | 4.61 | 25.9 | 35.7
5X6 | 0.7 | 1.25 | 1.8 | 20.5 | 925 | 3.08 | 32.9 | 44.8
5X10 | 0.7 | 1.6 | 1.8 | 24.6 | 1417 | 1.83 | 45.5 | 60.2
5X16 | 0.7 | 1.6 | 1.8 | 27.6 | 1812 | 1.15 | 58.8 | 77
5X25 | 0.9 | 1.6 | 1.9 | 32.2 | 2460 | 0.727 | 77 | 98
5X35 | 0.9 | 1.6 | 2 | 34.1 | 3019 | 0.524 | 94.5 | 119
5X50 | 1 | 2 | 2.2 | 39.7 | 4166 | 0.387 | 119 | 143.5
5X70 | 1.1 | 2 | 2.3 | 44.9 | 5443 | 0.268 | 150.5 | 175
5X95 | 1.1 | 2.5 | 2.5 | 51.3 | 7485 | 0.193 | 185.5 | 210
5X120 | 1.2 | 2.5 | 2.7 | 55.9 | 9026 | 0.153 | 217 | 241.5
5X150 | 1.4 | 2.5 | 2.8 | 61.4 | 10912 | 0.124 | 245 | 269.5
5X185 | 1.6 | 2.5 | 3 | 67.6 | 13119 | 0.0991 | 283.5 | 304.5
5X240 | 1.7 | 2.5 | 3.3 | 74.8 | 16427 | 0.0754 | 336 | 350
5X300 | 1.8 | 3.15 | 3.5 | 83.2 | 20915 | 0.0601 | 388.5 | 395.5
0.6/1kV-3+1 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+1X2.5 | 0.7/0.7 | 1.25 | 1.8 | 17.8 | 873 | 4.61/7.41 | 25.9 | 35.7
3X6+1X4 | 0.7/0.7 | 1.25 | 1.8 | 19.1 | 764 | 3.08/4.61 | 32.9 | 44.8
3X10+1X6 | 0.7/0.7 | 1.25 | 1.8 | 21.6 | 1002 | 1.83/3.08 | 45.5 | 60.2
3X16+1X10 | 0.7/0.7 | 1.6 | 1.8 | 25.1 | 1475 | 1.15/1.83 | 58.8 | 77
3X25+1X16 | 0.9/0.7 | 1.6 | 1.8 | 28.7 | 2101 | 0.727/1.15 | 77 | 98
3X35+1X16 | 0.9/0.7 | 1.6 | 1.8 | 30 | 2300 | 0.524/1.15 | 94.5 | 119
3X50+1X25 | 1/0.9 | 1.6 | 2 | 34.1 | 2945 | 0.387/0.727 | 119 | 143.5
3X70+1X35 | 1.1/0.9 | 2 | 2.1 | 39.2 | 4131 | 0.268/0.524 | 150.5 | 175
3X95+1X50 | 1.1/1.0 | 2 | 2.3 | 43.2 | 5199 | 0.193/0.387 | 185.5 | 210
3X120+1X70 | 1.2/1.1 | 2.5 | 2.4 | 48.8 | 6827 | 0.153/0.268 | 217 | 241.5
3X150+1X70 | 1.4/1.1 | 2.5 | 2.6 | 52.9 | 7915 | 0.124/0.268 | 245 | 269.5
3X185+1X95 | 1.6/1.1 | 2.5 | 2.7 | 57.8 | 9655 | 0.0991/0.193 | 283.5 | 304.5
3X240+1X120 | 1.7/1.2 | 2.5 | 2.9 | 64.1 | 11988 | 0.0754/0.153 | 336 | 350
3X300+1X150 | 1.8/1.4 | 2.5 | 3.1 | 69.8 | 14475 | 0.0601/0.124 | 388.5 | 395.5
0.6/1kV-4+1 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X4+1X2.5 | 0.7/0.7 | 1.25 | 1.8 | 18.9 | 731 | 4.61/7.41 | 25.9 | 35.7
4X6+1X4 | 0.7/0.7 | 1.25 | 1.8 | 20.3 | 875 | 3.08/4.61 | 32.9 | 44.8
4X10+1X6 | 0.7/0.7 | 1.6 | 1.8 | 23.9 | 1295 | 1.83/3.08 | 45.5 | 60.2
4X16+1X10 | 0.7/0.7 | 1.6 | 1.8 | 27 | 1712 | 1.15/1.83 | 58.8 | 77
4X25+1X16 | 0.9/0.7 | 1.6 | 1.9 | 31.2 | 2322 | 0.727/1.15 | 77 | 98
4X35+1X16 | 0.9/0.7 | 1.6 | 1.9 | 32.8 | 2759 | 0.524/1.15 | 94.5 | 119
4X50+1X25 | 1/0.9 | 2 | 2.1 | 38.5 | 3860 | 0.387/0.727 | 119 | 143.5
4X70+1X35 | 1.1/0.9 | 2 | 2.3 | 43 | 5010 | 0.268/0.524 | 150.5 | 175
4X95+1X50 | 1.1/1.0 | 2.5 | 2.4 | 48.9 | 6850 | 0.193/0.387 | 185.5 | 210
4X120+1X70 | 1.2/1.1 | 2.5 | 2.6 | 54 | 8395 | 0.153/0.268 | 217 | 241.5
4X150+1X70 | 1.4/1.1 | 2.5 | 2.7 | 58.4 | 9745 | 0.124/0.268 | 245 | 269.5
4X185+1X95 | 1.6/1.1 | 2.5 | 2.9 | 64.4 | 11948 | 0.0991/0.193 | 283.5 | 304.5
4X240+1X120 | 1.7/1.2 | 2.5 | 3.1 | 71.1 | 14832 | 0.0754/0.153 | 336 | 350
4X300+1X150 | 1.8/1.4 | 3.15 | 3.4 | 78.9 | 18826 | 0.0601/0.124 | 388.5 | 395.5
0.6/1kV-3+2 core copper conductor XLPE insulated steel wire armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Steel Wire diameter | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+2X2.5 | 0.7/0.7 | 1.25 | 1.8 | 18.6 | 705 | 4.61/7.41 | 25.9 | 35.7
3X6+2X4 | 0.7/0.7 | 1.25 | 1.8 | 20 | 845 | 3.08/4.61 | 32.9 | 44.8
3X10+2X6 | 0.7/0.7 | 1.25 | 1.8 | 22.5 | 1109 | 1.83/3.08 | 45.5 | 60.2
3X16+2X10 | 0.7/0.7 | 1.6 | 1.8 | 26.5 | 1630 | 1.15/1.83 | 58.8 | 77
3X25+2X16 | 0.9/0.7 | 1.6 | 1.8 | 30.2 | 2185 | 0.727/1.15 | 77 | 98
3X35+2X16 | 0.9/0.7 | 1.6 | 1.9 | 31.3 | 2505 | 0.524/1.15 | 94.5 | 119
3X50+2X25 | 1/0.9 | 2 | 2.1 | 37 | 3531 | 0.387/0.727 | 119 | 143.5
3X70+2X35 | 1.1/0.9 | 2 | 2.2 | 41.1 | 4572 | 0.268/0.524 | 150.5 | 175
3X95+2X50 | 1.1/1.0 | 2 | 2.4 | 45.8 | 5841 | 0.193/0.387 | 185.5 | 210
3X120+2X70 | 1.2/1.1 | 2.5 | 2.6 | 52.1 | 7765 | 0.153/0.268 | 217 | 241.5
3X150+2X70 | 1.4/1.1 | 2.5 | 2.7 | 55.4 | 8758 | 0.124/0.268 | 245 | 269.5
3X185+2X95 | 1.6/1.1 | 2.5 | 2.8 | 60.8 | 10777 | 0.0991/0.193 | 283.5 | 304.5
3X240+2X120 | 1.7/1.2 | 2.5 | 3 | 67.4 | 13385 | 0.0754/0.153 | 336 | 350
3X300+2X150 | 1.8/1.4 | 2.5 | 3.2 | 73.6 | 16100 | 0.0601/0.124 | 388.5 | 395.5